SECTION 11000 – ROTARY-LOBE POSITIVE DISPLACEMENT BLOWER SYSTEMS

Part	1.00 	GENERAL

- SUMMARY

The contractor shall install blower system(s) built by a qualified manufacturer. All components shall be furnished by a single manufacturer who shall be responsible for the performance and compatibility of the system.

- REFERENCES

American National Standards Institute (ANSI) B16.1, B40.1

American Society of Mechanical Engineers (ASME) PTC 9

American Gear Manufacturers Association (AGMA)

American Society of Testing and Materials (ASTM)

Anti-Friction Bearing Manufacturers' Association (AFBMA) 9, 11

American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE)

Institute of Electrical and Electronics Engineers (IEEE)

Mechanical Power Transmission Association

National Electrical Code (NEC)

National Electrical Manufacturers Association (NEMA) MG 1, ICS 6

National Fire Protection Association (NFPA) 70

Occupational Safety and Health Administration (OSHA)

Rubber Manufacturers Association (RMA)

Steel Structures Painting Council (SSPC)

Underwriters Laboratories (UL)

- SUBMITTALS

The submittals shall consist of a bill of material listing all components the system manufacturer will deliver; component Manufacturer's catalog cut sheets listing materials of construction, performance curves/charts, standards of design, warranty statement; prime/paint coating system plus the following information:

  - BLOWER

    - BHP at: normal system operating conditions

    - Discharge temperature at ambient temperature and normal system        operating conditions.

    - L10 bearing life calculations for each bearing.

  - MOTOR

    - 1/2, 3/4, full load efficiencies and power factors

    - L10 bearing life calculations for each bearing.

  - SILENCERS

    - An attenuation performance curve for each type of silencer.

  - PRESSURE RELIEF VALVE

    - Set pressure

  - Shop drawings of assembled system stating what items will be shipped to the job site assembled and those shipped loose for field assembly.

  - V-belt drive calculations.

  - A list of all exceptions and an explanation of each non-compliance with the specifications.

- QUALITY ASSURANCE

  - The blower system(s) will be built by a blower system supplier who has units at 50 or more waste water treatment plants, the same size or larger than those specified below, that have been in successful operation for fifteen or more years.

  - All components shall be furnished by a single supplier who shall be responsible for the performance and compatibility of the system.

  - The blower system manufacturer shall be an authorized warranty service center for the bare blower provided.

  - Unnamed manufacturers shall provide a complete technical submittal to the engineer for review at least 15 days prior to the published bid date noting all project specific system performances, curves, drawings, maintenance requirements, and any non-compliances with the specification to qualify for use on the project.

  - Blowers, motors, and all primary components shall be manufactured in the United States with replacements and parts available from multiple sources within the United States.

- STORAGE & HANDLING

  - Care must be taken during unloading and handling of equipment to ensure against undue strain to the blower and motor.  DO NOT use lifting straps or chains under the blower or motor.  Lift from under the main frame, base or use base mounted lifting lugs (if provided).

  - In storage blowers must be kept clean, free of moisture and rotated a minimum of 20 revolutions each week to maintain warranty. For storage in excess of four months, or in a damp or corrosive environment see the manufacturer's operation and maintenance manual.

- CONDITIONS OF SERVICE

| APPLICATION: |  |
| --- | --- |
| NUMBER OF BLOWERS: |  |
| SITE ELEVATION, FASL: |  |
| MAXIMUM INLET TEMPERATURE, ºF: |  |
| MAXIMUM RELATIVE HUMIDITY, %: |  |
| SCFM ± 4 %: |  |
| DIFFERENTIAL PRESSURE, PSIG: |  |
| MAX BHP REQUIRED: |  |
| RPM LIMIT AT ABOVE SCFM: |  |
| MOTOR SIZE: |  |
| SOUND LIMIT REQ. @ 1 METER IN FREE FIELD: |  |

- WARRANTY

  - STANDARD WARRANTY

The manufacturer will provide a warranty stating that the blower system is warranted to be in accordance with the product specifications mutually agreed upon and to be free from defects in workmanship and materials. The blower system manufacturer’s product warranty will extend to all products supplied by the blower system manufacturer whether or not manufactured by the blower system manufacturer. This warranty shall terminate at twelve (12) months in service with the original user or eighteen (18) months from the date of shipment, whichever occurs first.

(OPTIONAL EXTENDED WARRANTY)

  - EXTENDED WARRANTY

The manufacturer will provide a warranty stating that the blower system is warranted to be in accordance with the product specifications mutually agreed upon and to be free from defects in workmanship and materials. The blower system manufacturer’s product warranty will extend to all products supplied by the blower system manufacturer whether or not manufactured by the blower system manufacturer. This warranty shall be in effect provided that the customer adheres to the warranty requirements. This warranty shall terminate five years from the date of shipment.

PART 	2.00 	PRODUCTS

- MANUFACTURERS

  - The blower system(s) shall be model 3C-PAC, manufactured by Universal Blower Pac, Inc., Noblesville, Indiana.

- CONSTRUCTION

  - BLOWER

The blower shall be able to accommodate the pressure and flow described above in section 1.06 Conditions of Service.  The blower shaft shall be one piece, separate or cast integrally with the impellers. Blower shall be equipped with projecting glass viewports with brass bodies for easy oil level indication from multiple angles. Blowers shall be dynamically balanced and provide oil free non-contact compression.

    - ATTENUATION

      - Each blower system shall be equipped with an acoustical enclosure. The Enclosures shall be designed, assembled and inspected by Universal Blower Pac, Inc. at the manufacturing site with documentation provided to verify the noise reduction demanded in these documents. Noise attenuation shall be provided as necessary to reach the specified sound limit requirement at a distance of 1 meter from the operating equipment in a free field environment. All readings shall be taken by personnel experienced in the field of sound attenuation.

      - The enclosure herein specified shall be designed and manufactured by the blower system manufacturer specifically for the equipment supplied. Units shall be designed to be picked up by a fork truck. Each acoustical enclosure shall be shipped completely assembled. No field assembly shall be permitted

      - Absorption of sound waves shall be the basis of design for the enclosure. The complete blower system will be enclosed to meet the level specified. With absorption considered, perforated metal inner skin retaining devices shall not be considered acceptable.

      - Absorption media shall be a nominal 2-inch thick resilient material capable of returning to its original form after compression. Media shall have an overall weight of not less than 1.6 pounds per cubic foot. Media sheets shall have an upper oil resistant layer a minimum of three mils in thickness to protect the integrity of the media. Absorption media shall be interior and be fitted to each exterior facet and show contact at all points. Media shall be snug fit, be complete with pressure sensitive adhesive and held in place with washers, studs and cap nuts manufactured from corrosive resistant materials. All adhesives used in anchoring studs or other items in structure shall be high temperature industrial material rated for the application.

      - Outer skin shall be a minimum 14 gauge galvannealed steel.  Enclosure panels to be 10 gauge aluminum.  Lesser gauges shall not be acceptable.  All surfaces are to be powder coated per section 2.02.I. Coatings.

      - No fastening hardware shall be visible on the exterior of the enclosure except those holding the instruments and relief valve exhaust differ in place for ease of repair.  Rivets or loose fitting panels which can loosen during operation will not be accepted. Slide-in panels showing a loose fit shall provide grounds for rejection.

      - Each enclosure will have removable service panels.  All surfaces and edges shall be free of burs and sharp edges.  Panels shall lock closed using key-operated compression latches with folding handles that fit flush.

      - Each enclosure shall incorporate internal acoustical-lined intake-air vent boxes rated for the SCFM listed in the "service" section and discharge pipe openings with sound seal.  Louvers shall not be acceptable.

      - A 120/60/1 electric cooling fan with thermostat control and acoustical vent shall be supplied installed on the enclosure. To ensure adequate cooling at all speeds the cooling fan will not be connected to the blower or motor shaft in any way.

  - MOTOR

| DESIGN: | B, squirrel-cage, induction per NEMA MG1 & IEEE standards |
| --- | --- |
| HP: | Nameplate greater than the brake horsepower at 10% above the relief valve set pressure as described in 1.03 D 2. |
| RPM: | 1800 |
| TYPE: | TEFC |
| POWER: | 460 Volt, 3 phase, 60 Hertz |
| INSULATION: | Class F with class B rise |
| SERVICE FACTOR: | 1.15 ( or 1.0 if used in conjunction with VFD) at power voltage and site elevation listed above |
| EFFICIENCY: | "premium efficient" per latest edition of NEMA MG1 |

(OPTIONAL, THERMOSTATS)

    - Motor(s) shall have_______ (thermostats, thermistors, RTDs) for over temperature protection.

(OPTIONAL, SPACE HEATERS)

    - Motor(s) shall have 120 volt single phase space heaters

(OPTIONAL, VARIABLE FREQUENCY DRIVE)

    - The motor will be designed, constructed, warranted for two year operation by a constant-torque variable frequency drive for 10:1 turn down. The insulation shall meet or exceed the current NEMA MG1-31.4.4.2 and have a Class F thermostat in each phase.  Motor and variable frequency drive must be capable of starting, accelerating and maintaining blower operating speed within the specified operating range on a continuous basis without overheating.

  - V-BELT

    - High-capacity type, oil and heat resistant, static-dissipating drive belts selected to have a 1.4 or higher service factor above the required blower brake horsepower. Sheaves shall mount to the blower and motor shafts with QD type bushings.

(OPTIONAL, ADDITIONAL SPEEDS)

    - Additional drive components shall be supplied to deliver ___ CFM. (list as many different flow rates as needed)

  - DRIVE GUARD

The guard shall be fabricated steel with openings on the front designed to allow ample ventilation for the drive, have an easy access cover and conform to applicable safety codes.

  - BASE

    - Base shall include spring loaded auto-tension device for ease of drive installation and maintenance.  Covered forklift slots shall be integral to the base design.

    - The blower base shall have isolation mounts to minimize transmitted vibrations from the blower system to the surrounding structure.

  - ACCESSORIES

    - INLET FILTER/SILENCER

Each blower will have a filter/silencer with paper media that removes 99.5% of 2 micron particles.  The maximum pressure drop across the clean element shall be less than 2-inches of water column.  The filter/silencer shall be Stoddard FH64 or equal.

    - DISCHARGE SILENCER

Silencers shall be of the helical-flow design and separate from the base frame. Air velocity shall be 5500 to 7000 feet per minute.  Silencer shall be Universal series CB or equal.

    - FLEXIBLE JOINT

      - Each blower shall have a flexible joint located between the blower and discharge silencer to minimize vibration transmission to downstream piping.  The joint’s elastomer must be rated higher than the maximum expected service temperature and pressure.

      - Each blower shall have an external discharge flexible joint that matches the blower discharge silencer size. The joint’s elastomer must be rated higher than the maximum expected service temperature and pressure. The flexible joint shall ship installed on the system.

  - VALVES

    - PRESSURE RELIEF VALVE

Each blower shall be protected by a spring loaded pressure relief valve preset to start opening at half a PSIG above the PSIG listed in the "service" section, be full open at not more than 10% above the set pressure, and rated for the SCFM and PSIG listed in the "service" section.  If the valve malfunctions it shall do so in the open condition to prevent blower damage. Valve shall vent outside of the enclosure.

    - CHECK VALVE

Each blower shall have a discharge check valve. Valves 6-inch and smaller shall have a NPT steel body. Valves 8-inch and larger shall have a cast-iron wafer body. Internals shall be aluminum split discs with no-pinch elastomer and seal rated above the maximum anticipated discharge temperature.  Valve shall be shipped installed on the system.

(OPTIONAL)

    - ISOLATION VALVE

Each blower shall have a discharge isolation valve.  Valves less than two inches in diameter will be ball valves.  Valves 2-inches and larger shall be cast-iron wafer-body butterfly type with a locking handle. The temperature rating of the seat must exceed the maximum anticipated discharge temperature.  The valve shall be shipped installed on the system.

(OPTIONAL FOR AIR SCOUR APPLICATION)

    - BLOW-OFF VALVE & SILENCER

Each blower shall have an open to atmosphere blow-off valve with actuator & silencer. The valve will automatically be closed after the motor has reached operating speed by a 120/1/60 electric actuator. The valve shall be Keystone model 221 or equal. A silencer shall be supplied with each blow-off valve to mitigate high frequency noise. The silencer shall be high grade type, rated for venting applications. The silencer shall be Universal Silencer model SU5 or equal. The unloading valve and silencer shall be two pipe sizes larger than the pressure relief valve's inlet port. The valve and silencer shall ship loose for field installation.

  - INSTRUMENTS

    - PRESSURE GAUGE

Each blower shall have a 2-1/2" diameter, stainless steel case, brass bourdon tube, liquid filled, 1/4 NPT connection pressure gauge with a 0-15 PSIG scale on systems operating up to 10 PSIG and 0-30 PSIG for higher pressures.  Gauge shall have a 1/4" brass snubber and isolation valve and be mounted in the enclosure wall. Gauge shall be Winters 901 or equal.

    - FILTER RESTRICTION GAUGE

Each inlet filter/silencer shall have a gauge, with isolation valve, to measure vacuum in the filter element. The gauge shall have a visual indicator to lock at the current vacuum when the blower is shut off and have a manual reset. Gauge shall be mounted in the enclosure wall. Gauge shall be Dwyer Magnehelic or equal.

    - THERMOMETER

Each blower shall have a 4.5" diameter thermometer with a 50-300 ºF scale on systems up to 10 PSIG, 50-500 ºF for higher pressure. Thermometer shall be mounted in the enclosure wall. The thermometer shall be Wika TI.V45RB or equal.

(OPTIONAL REPLACES THERMOMETER)

    - THERMOMETER / TEMPERATURE SWITCH

Each blower shall have a high discharge air temperature switch and thermometer. The thermometer shall have an easy to read 3-1/4” dual scale dial thermometer and a 3A 250VAC / 2A 250VDC SPDT relay in a 304 stainless steel housing. Color coordinated pointers display the current process temperature and set point. A front adjustment knob controls the set pointer. The internal mechanical switch movement prevents the set point pointer from sticking to the process indicating pointer. Brass wetted internal materials have 3 percent accuracy. The thermometer shall have a 10.5’ stainless steel capillary with ½” NPT process connection. The electrical connections shall be finger-safe screw terminals. The instrument shall be mounted in the enclosure wall. The instrument shall be Dwyer RRT3300U or equal.

(OPTIONAL)

    - PRESSURE SWITCH

Each blower shall have a NEMA 4X, SPDT 15 A 125/250/480 VAC resistive-contact high-discharge pressure switch. The switch shall be set half a PSIG below the blower's maximum operating pressure.

(OPTIONAL)

    - FILTER DIFFERENTIAL VACUUM SWITCH

Each filter shall have a NEMA 3R, SPDT 15A 125/250/480 VAC resistive contact differential vacuum switch factory preset at 20" WC vacuum.

(OPTIONAL)

    - CONTROL PANEL

Each blower system shall have a factory-mounted and wired NEMA 3R control panel.  Each panel shall have NEMA rated components (combination starter, circuit breaker with interlocking door handle, 3-leg motor overload protection, 120 volt control transformer, door mounted overload reset pushbutton, door mounted run indicating light, door mounted HOA selector switch, door mounted elapsed-time meter, enclosure cooling fan power/control, and terminals for field connection).

    - REPLACEMENT PARTS

Each blower shall be furnished with the following spare parts:

One spare filter element

One set of spare V-belts

Lubricants for start-up (6 months, 1 year)

  - COATINGS

Equipment shall be cleaned to SSPC-SP 3 and receive a 2-3 mil DFT shop coat of Coroteck 131 universal primer. The systems shall then receive a finish coat of Coroteck 220 alkyd enamel, 50% gloss, high temperature paint. The coat shall be 2-3 mil DFT.

Enclosures shall be powder coated with a coating that is highly resistant to UV rays and weather.  Tiger Drylac Series 38 super durable or equal.

  - MANUALS

Operation and maintenance manuals shall be provided for each size of blower. One copy will ship with the system to the job site.

PART 	3.00	EXECUTION

- ERECTION/INSTALLATION APPLICATION

  - The following points must be followed to ensure an adequate installation:

    - The blower pad must be located on the equivalent of compacted soil substructure, which will allow the pad to remain flat, rigid, and free of resonant frequencies within the operating range of the equipment.

    - The blower must be anchored using bolts intended specifically for dynamic loading.

    - The unit must be installed and leveled per the manufacturer’s instructions supplied in the O&M manual.

- START-UP AND TESTING

  - The blower system supplier shall provide the services of a factory trained technician to check installation, verify proper operation and train the owner’s personnel in proper maintenance procedures.  Start-up services shall be a minimum of one day for every three blower systems.

(OPTIONAL)

  - A PTC-9 slip test report shall be supplied for each size of blower.